# SECTION 16135

ELECTRICAL BOXES AND FITTINGS

# PART 1 - GENERAL

1.01	DESCRIPTION OF WORK:

A.		Extent of electrical box and electrical fitting work is indicated by drawings and schedules.

1.02	RELATED DOCUMENTS AND SECTIONS:

A.		Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specification sections, apply to work of this section.

B.		This section is a Division 16 Basic Materials and Methods section and is part of each Division 16 section making reference to electrical wiring boxes and fittings specified herein.

1.03	REFERENCES FOR QUALITY ASSURANCE:

A.		UL Compliance: Comply with applicable requirements of UL 50, UL 514-Series, and UL 886 pertaining to electrical boxes and fittings.  Provide electrical boxes and fittings, which are UL-listed and labeled.

B.		NEMA Compliance: Comply with applicable requirements of NEMA Stds/Pub FB1, No.’s OS1, OS2, and Pub 250 pertaining to outlet and device boxes, covers and box supports.

C.		NECA:  Comply with Standard of Installation.

1.04	SUBMITTALS FOR CLOSEOUT:

A.		Record actual locations and mounting heights of pull and junction boxes on project red-lined as-built drawings.

PART 2 - PRODUCTS

2.01	FABRICATED BOXES:

A.	Surface Mounted Weatherproof Outlet Box:  Provide UL listed rugged, seamless, “FS”, “FD” or die cast aluminum, electrostatic painted with a baked weather resistant powder finish, 2½” x 2¾ x 2” deep box that will accept a single gang weatherproof cover or standard “FS” cover.  The box shall have external mounting ears such that the back of the box fits flat on the mounting surface.  Box may have knockout studs on back of box to provide alternate means for wall mounting.  Box shall have threaded hub outlets for conduits and connectors.  Threaded closure plugs shall be used to seal up all un-used openings.  Deeper boxes or box extension shall be used to increase box volume to comply with NEC fill requirements.

B.		Junction and Pull Boxes:  Boxes shall be NEMA 12 for indoor. Boxes shall be NEMA 4XSS for outdoor applications with appropriate cover fastened with stainless steel fasteners, unless indicated otherwise.  Provide UL listed box and cover of type, shape and size as required.

C.		Hubs: Provide Myers hubs, grounding type, on all enclosures. Provide corrosion-resistant box knockout closures where required. Provide conduit offset connectors etc., of types and sizes, to suit respective installation requirements and applications.

PART 3 - EXECUTION

3.01	INSTALLATION OF ELECTRICAL BOXES AND FITTINGS:

A.		General:  Verify locations of boxes and outlets prior to rough-in.  Install electrical boxes and fittings where indicated, complying with manufacturer’s written instructions, applicable requirements of NEC and NECA’s “Standard of Installation,” and in compliance with recognized industry practices to ensure that products fulfill requirements.

B.		Coordinate installation of electrical boxes and fittings with wire/cable and raceway installation work.

C.		Provide weatherproof outlet boxes for interior and exterior locations exposed to weather or moisture.

D.		Provide knockout closures to cap unused knockout holes where blanks have been removed.

E.		Install junction and pull boxes and conduit bodies in those locations that ensure ready accessibility.

F.		DO NOT install aluminum products in concrete.

G.		Subsequent to installation of boxes, protect boxes from construction damage and vacuum clean all interior debris from enclosure.

H.		Electrical boxes are shown on drawings in approximate locations unless dimensioned.  Relocate box, under base bid, up to 10 feet if required to accommodate intended purpose.

I.		Maintain headroom and present neat mechanical appearance.

J.		Support boxes independently of conduit.

K.		Use cast outlet box in exterior locations exposed to the weather and wet locations.

L.		Large Pull Boxes:  Use NEMA 12 enclosure for interior dry locations, surface-mounted stainless steel NEMA 4X enclosure in other locations.

3.02	INTERFACE WITH OTHER PRODUCTS:

A.		Coordinate installation of outlet box for equipment connections.

3.03	ADJUSTING

A.		Install knockout closures in unused box openings.

3.04	CLEANING

A.		Clean interior of boxes to remove dust, debris and other material.

B.		Clean exposed surfaces and restore finish.

3.05	GROUNDING:

A.		Upon completion of the installation, properly ground electrical boxes and demonstrate compliance with requirements as specified.

## END SECTION -