SECTION 03350

CONCRETE FINISHES

PART 1	GENERAL

1.01	SCOPE OF WORK

A.	Furnish all labor, materials, equipment and incidentals required and finish cast-in-place concrete surfaces as shown on the Drawings and as specified herein.

1.02	RELATED WORK

A.	Concrete Formwork is included in Section 03100.

B.	Cast-In-Place Concrete is included in Section 03300.

C.	Grout is included in Section 03600.

D.	Painting, toppings and special surfaces are included in Division 9.

1.03	SUBMITTALS

A.	Submit, in accordance with Section 01300, shop drawings and product data showing materials of construction and details of installation for:

1.	Concrete sealer.  Confirmation that the sealer is compatible with additionally applied coatings shall also be submitted.

2.	Chemical hardener. Confirmation that the hardener is compatible with sealer shall also be submitted.

1.04	REFERENCE STANDARDS

A.	American Society for Testing and Materials (ASTM)

1.	ASTM C33 - Standard Specification for Concrete Aggregates.

B.	Where reference is made to one of the above standards, the revision in effect at the time of bid opening shall apply.

1.05	QUALITY ASSURANCE

A.	Finishes

1.	For concrete which will receive additional applied finishes or materials, the surface finish specified is required for the proper application of the specified manufacturer's products.  Where alternate products are approved for use, determine if changes in finishes are required and provide the proper finishes to receive these products.

2.	Changes in finishes made to accommodate products different from those specified shall be performed at no additional cost to the Owner.  Submit the proposed new finishes and their construction methods to the Engineer for approval.

B.	Services of Manufacturer's Representative

1.	Make available at no additional cost to the Owner, upon 72 hours notification, the services of a qualified field representative of the manufacturer of sealer or hardener to instruct the user on the proper application of the product under prevailing job conditions.

PART 2	PRODUCTS (NOT USED)

PART 3	EXECUTION

3.01	FORMED SURFACES

A.	Forms shall not be removed before the requirements of Section 03300 have been satisfied.

B.	Exercise care to prevent damaging edges or obliterating the lines of chamfers, rustications or corners when removing the forms or performing any other work adjacent thereto.

C.	Prepare the exposed surface as specified in Section 03300.

D.	Rough-Form Finish

1.	No additional finishing is required.

E.	Rubbed Finish

1.	While the wall is still damp, apply a thin coat of medium consistency neat cement slurry by means of bristle brushes to provide a bonding coat within all pits, air holes or blemishes in the parent concrete.  Avoid coating large areas with the slurry at one time.

2.	Before the slurry has dried or changed color, apply a dry (almost crumbly) grout proportioned by volume and consisting of one part cement to 1-1/2 parts of clean masonry sand having a fineness modulus of approximately 2.3 and complying with the gradation requirements of ASTM C33 for such a material.  Grout shall be uniformly applied by means of damp pads of coarse burlap approximately 6-in square used as a float.  Scrub grout into the pits and air holes to provide a dense mortar in all imperfections.

3.	Allow the mortar to partially harden for one or two hours depending upon the weather.  If the air is hot and dry, keep the wall damp during this period using a fine, fog spray.  When the grout has hardened sufficiently so it can be scraped from the surface with the edge of a steel trowel without damaging the grout in the small pits or holes, cut off all that can be removed with a trowel.  (Note:  Grout allowed to remain on the wall too long will harden and will be difficult to remove.)

4.	Allow the surface to dry thoroughly and rub it vigorously with clean dry burlap to completely remove any dried grout.  No visible film of grout shall remain after this rubbing. The entire cleaning operation for any area must be completed the day it is started. Do not leave grout on surfaces overnight.  Allow sufficient time for grout to dry after it has been cutoff with the trowel so it can be wiped off clean with the burlap.

5.	On the day following the repair of pits, air holes and blemishes, the walls shall again be wiped off clean with dry, used pieces of burlap containing old hardened mortar which will act as a mild abrasive.  After this treatment, there shall be no built-up film remaining on the parent surface.  If, however, such a film is present, a fine abrasive stone shall be used to remove all such material without breaking through the surface film of the original concrete.  Such scrubbing shall be light and sufficient only to remove excess material without changing the texture of the concrete.

6.	A thorough wash-down with stiff bristle brushes shall follow the final bagging or stoning operation.  No extraneous materials shall remain on the surface of the wall.  The wall shall be sprayed with a fine fog spray periodically to maintain a continually damp condition for at least three days after the application of the repair grout.

3.02	FLOORS AND SLABS

A.	Floated Finish

1.	Machine Floating

a.	Screed floors and slabs with straightedges to the established grades shown on the Drawings.  Immediately after final screeding, a dry cement/sand shake in the proportion of two sacks of portland cement to 350 lbs. of coarse natural concrete sand shall be sprinkled evenly over the surface at the rate of approximately 500 lbs./1,000 sq. ft. of floor.  Do not sprinkle neat, dry cement on the surface.

b.	The application of the cement/sand shake may be eliminated at the discretion of the Engineer if the base slab concrete exhibits adequate fattiness and homogeneity and the need is not indicated.  When the concrete has hardened sufficiently to support the weight of a power float without its digging into or disrupting the level surface, thoroughly float the shake into the surface with a heavy revolving disc type power compacting machine capable of providing a 200 lb. compaction force distributed over a 24-in diameter disc.

c.	Start floating along walls and around columns and then move systematically across the surface leaving a matte finish.

d.	The compacting machine shall be the "Kelly Power Float with Compaction Control" as manufactured by Kelley Industries of SSP Construction Equipment Inc., Pomona, CA or equal.  Troweling machines equipped with float (shoe) blades that are slipped over the trowel blades may be used for floating.  Floating with a troweling machine equipped with normal trowel blades will not be permitted.  The use of any floating or troweling machine which has a water attachment for wetting the concrete surface during finishing will not be permitted.

2.	Hand Floating

a.	In lieu of power floating, small areas may be compacted by hand floating.  The dry cement/sand shake previously specified shall be used unless specifically eliminated by the Engineer.  Screed the floors and slabs with straightedges to the established grades shown on the Drawings.  While the concrete is still green, but sufficiently hardened to support a finisher and kneeboards with no more than 1/4-in indentation, wood float to a true, even plane with no coarse aggregate visible.  Use sufficient pressure on the wood floats to bring moisture to the surface.

3.	Finishing Tolerances

a.	Level floors and slabs to a tolerance of plus or minus 1/8-in when checked with a 10-ft straightedge placed anywhere on the slab in any direction.  Where drains occur, pitch floors to drains such that there are no low spots left undrained.  Failure to meet either of the above requirements shall be cause for removal, grinding, or other correction as directed by the Engineer.

B.	Broom Finish

1.	Screed slabs with straightedges to the established grades indicated on the Drawings.  When the concrete has stiffened sufficiently to maintain small surface indentations, draw a stiff bristle broom lightly across the surface in the direction of drainage, or, in the case of walks and stairs, perpendicular to the direction of traffic to provide a non-slip surface.

C.	Steel Trowel Finish

1.	Finish concrete as specified in Paragraph 3.02A.  Then, hand steel trowel to a perfectly smooth hard even finish free from high or low spots or other defects.

3.03	APPROVAL OF FINISHES

A.	All concrete surfaces, when finished, will be inspected by the Engineer.

B.	Surfaces which, in the opinion of the Engineer, are unsatisfactory shall be refinished or reworked.

C.	After finishing horizontal surfaces, regardless of the finishing procedure specified, the concrete shall be cured in compliance with Section 03300 unless otherwise directed by the Engineer.

3.04	SCHEDULE OF FINISHES

A.	Concrete shall be finished as specified either to remain as natural concrete to receive an additional applied finish or material under another section.

B.	Concrete for the following conditions shall be finished as noted on the Drawings and as further specified herein:

1.	Concrete to receive dampproofing or waterproofing:  Rough-form finish.  See Paragraph 3.01D above.

2.	Concrete not exposed to view and not scheduled to receive an additional applied finish or material:  Rough-form finish.  See Paragraph 3.01D above.

3.	Exterior vertical concrete above grade exposed to view:  Rubbed finish.  See Paragraph 3.01E above.

4.	Interior vertical concrete exposed to view except in water containment areas:  Rubbed finish. See Paragraph 3.01E above.

5.	Vertical concrete in water containment areas.  Rubbed finish on exposed surfaces and extending to two feet below ground level:  Rough-form finish on remainder of submerged areas.  See Paragraphs 3.01E and 3.01D above.

6.	Interior and exterior underside of concrete exposed to view: Rubbed finish.  See Paragraph 3.01E above.

7.	Interior or exterior horizontal concrete not requiring floor hardener or sealer:  Floated finish.  See Paragraph 3.02A above.

8.	Concrete for exterior walks, interior and exterior stairs:  Broomed finish perpendicular to direction of traffic.  See Paragraph 3.02B above.

9.	Concrete slabs on which process liquids flow or in contact with sludge: Steel trowel finish.  See Paragraph 3.02C above.

10.	Concrete structure bottoms to be covered with grout:  See Section 03600.

11.	Concrete to be coated or painted:  See Division 9.

END OF SECTION