SECTION 16902

ELECTRIC CONTROLS AND RELAYS

PART 1 - GENERAL

1.1	REFERENCES

A.	NEMA ICS 1 - General Standards for Industrial Control Systems.

B.	NEMA ICS 2 - Standards for Industrial Control Devices, Controllers and Assemblies.

C.	NEMA ICS 6 - Enclosures for Industrial Controls and Systems.

D.	NEMA ST 1 - Standard for Specialty Transformers (Except General Purpose Type.)

E.	NFPA 70 - National Electrical Code.

1.2	SUBMITTALS

A.	Shop Drawings:  Submit starter and control panel layouts, wiring connections and diagrams, dimensions, and support points.

B.	Product Data:  Provide for each component showing electrical characteristics and connection requirements.

C.	Manufacturer's Installation Instructions:  Include instructions for storage, handling, protection, examination, preparation, installation, and start-up of Product.

1.3	QUALIFICATIONS

A.	Manufacturer:  Company specializing in manufacturing the Products specified in this section with minimum five years documented experience and with service facilities within 100 miles of Project.

1.4	REGULATORY REQUIREMENTS

A.	Conform to requirements of NFPA 70.

B.	Furnish components of product listed and classified by Underwriters Laboratories, Inc. as suitable for purpose specified and indicated.

PART 2 - PRODUCTS

2.1	PUSHBUTTONS AND SELECTOR SWITCHES

A.	Manufacturers:  Square D - Type K, CL9001, or equivalent from Allen Bradley or Eaton.

B.	Contacts:  NEMA ICS 2, Form C.

C.	Contact Ratings:  NEMA ICS 2, A600 for AC and P600 for DC.

D.	Selector Switches Operators:  Multi-position rotary selector switch as indicated on drawings.

E.	Pushbutton Operator:  Shrouded type, 30.5mm size.

F.	Starters and Control Stations:  Heavy duty oiltight type pushbutton station.

2.2	PILOT LIGHTS

A.	Manufacturers:  Square D - Type K, CL9001, or equivalent from Allen Bradley or Eaton.

B.	Type:  LED – 30.5mm size, Push-to-test (PTT), suitable for the enclosure.

C.	Voltage:  Same as secondary of Control Power Transformer.

2.3	CONTROL RELAYS

A.	Manufacturers:  Square D - CL8501, Type K or equivalent from Allen Bradley or Eaton.

B.	Relays:  NEMA ICS 2, general purpose, tube base with pin terminals and internal LED pilot light.

C.	Contacts:  NEMA ICS 2, Form C.

D.	Contact Ratings:  NEMA ICS 2, Class A600.

E.	Coil Voltage:  Same as secondary of Control Power Transformer.

F.	Base:  Octal.

2.4	CONTACTORS

- Manufacturers: Square D, S Series, or equivalent from Allen Bradley or Eaton.

- Arrangement: Contacts rated for HP and full load current of motor controlled, at voltage of motor.  Reversing types have contacts that are mechanically and electrically interlocked.

- Coil Voltage:  Same as secondary of Control Power Transformer.

- Accessories: (2) N.O. and (2) N.C. aux contacts.

2.5	OVERLOAD RELAYS

- Manufacturers: Square D, Motor Logic Series, or equivalent from Allen Bradley or Eaton.

- Description: Solid state overload disconnects all 3 phases whenever there is over-current, phase loss, or phase unbalance.

- Adjustment and Operation: Field-adjustable in range of amperages for size starter provided.  Overload shall not be affected by ambient temperatures.

## 2.6	TERMINAL BLOCKS

### A.	NEMA ICS 4.

### C.	Power Terminals:  Unit construction type with closed back and tubular pressure screw connectors, rated 30 amp 600 volts.

### D.	Signal and Control Terminals:  Modular construction type, suitable for channel mounting, with tubular pressure screw connectors, rated 300 volts, 20 amps.

### E.	Provide grounding bus terminal block, with adequate terminals for each grounding conductor and bond terminal block to metal of enclosure.

2.7	CONTROL POWER TRANSFORMER

A.	Manufacturers:  Square D. or equivalent from Allen Bradley or Eaton.

B.	Description:  NEMA ST 1, machine tool transformer with isolated secondary winding.

C.	Power Rating:  Standard VA rating, unless capacity indicated otherwise on the plans.

D.	Voltage Rating:  Secondary voltage shall be 120-volts, single phase.

E.	Fuses:  Provide primary and secondary fuses.

2.8	ENCLOSURES

- Starters: NEMA ICS 6, Type 12.

- Enclosure Finish:  Manufacturer's standard enamel.

- Provide metal barriers to form separate compartments wiring of different systems and voltages.

2.9	WIRING AND DEVICES

A.	All control wiring shall be #14 AWG stranded copper, 600V, 90 deg. C type THHN/THWN, color coded as follows:

1.	A.C.-hot circuits	Black

2.	A.C.-neutral circuits	White

3.	A.C.-control circuits	Red

4.	Equipment ground	Green

B.	All 480 volt wiring shall be 12 gauge min. brown/orange/yellow.

C.	All components and wiring materials shall be UL (Underwriter’s Lab.) listed and UL labeled for its intended use.

D.	Devices and assembled controls shall bear the manufacturer’s name, phone number and date of manufacture.

PART 3 - EXECUTION

3.1	INSTALLATION

A.	Conductors shall be bundled to keep them in place.  All wiring leaving from a bundle to a device shall be serviced looped.

B.	Tag all wiring with numbers.  Tagging shall be done with slip-on sleeve wire markers.  Wrap around tape will not be acceptable.  Tags shall match wire size.  All markers shall read “left to right” or “top to bottom”.

C.	Connect all control wiring from external devices to terminal blocks.

D.	Do not splice wires.  If necessary, because of component pigtails, suitable terminal blocks shall be furnished.

E.	Tag all components with engraved 1/6” thick laminated plastic markers.  Markers shall be secured to the mounting panel or inside surface of door with RTV type class silicone sealant, completely covering the rear of the label.  Markers shall not be mounted on the component.

F.	Remove sharp edges, burrs, rough surfaces or threads from conduit fittings, raceways, or any other parts, which may come into contact with the insulation of the conductors.  Where necessary, additional protection consisting of a flame retardant, oil resistant insulating materials shall be provided to protect conductor insulation.

G.	Test each circuit for continuity, short circuits and ground faults when all wiring of the electrical system is complete.

H.	Install components (products) in accordance with manufacturer's instructions.

I.	Install individual relays in enclosures.

J.	Install all associated wiring appurtenances:  wireways, equipment fasteners, wire, straps, markers and lugs as required under 1.3 References.

- END SECTION -