SECTION 02220

GENERAL EXCAVATION

# GENERAL

## 1-01	SCOPE:

### Summary of Work:  The CONTRACTOR shall furnish all labor, materials, and equipment to perform the excavation and backfilling as needed to construct the flood proofing improvements on the North and South ends of the Marvin Braud Pumping Station as shown on the Drawings.

### Related work specified in other sections:

#### All Sections in Technical Specifications

## 1-02	APPLICABLE PUBLICATIONS:

### A.	American Society of Testing Materials (ASTM)

#### 1.	D698 Standard Test Methods for Laboratory compaction Characteristics of Soil Using the Standard Effort (56,000 ft-lbf/cu. ft.)

#### 2.	D1557 Standard Test Methods for Laboratory compaction Characteristics of Soil Using the Modified Effort (12,400 ft-lbf/cu. ft.)

#### 3.	D4253 Standard Test Methods for Maximum Index Density and Unit Weight of Soils Using a Vibratory Table

#### D4254 Standard Test Method for Minimum Index Density and Unit Weight of Soils and Calculation of Relative Density

### B.	Louisiana Department of Transportation

#### 1.	Standard Specifications for Road and Bridge Construction, latest edition, (LDOT)

### Miscellaneous Project Data:

#### Project geotechnical report – copy on file with Engineer

## 1-03	SUBMITTALS:

## The CONTRACTOR shall submit, prior to the start of work, the planned method of construction of the south floodwall extension and the north floodwall extension as shown on the Drawings, or as specified herein, for the ENGINEER's review.  This plan shall also indicate the intended construction sequence for removal of septic tank, any dewatering, backfilling and installation of a new septic tank.

## 1-04	CERTIFICATIONS AND TESTING:

## A.	Field density tests in accordance with ASTM Standards, for each type of material used in backfilling may be required.  Failure to meet the specified density will require the CONTRACTOR to recompact and retest, at its own expense, those areas directed by the ENGINEER.

## 1-05	INSPECTION COORDINATION:

## A.	The CONTRACTOR shall provide access to the WORK for the ENGINEER as requested for inspection.  The CONTRACTOR shall provide 48 hours notice of its intention to begin new WORK activities.

# PRODUCTS

## 2-01	BACKFILL:

## A.	The placement of the embankment on both sides of the concrete floodwall, around new septic tank and the north end concrete grade beam is backfill. The toe of the embankment shall tie into the existing ground line as shown on the plan drawings.

# EXECUTION

## 3-01	SITE PREPARATION:

### Clearing and Grubbing:  The CONTRACTOR shall perform clearing and grubbing in accordance with the following provisions:

#### Perform only in areas where earthwork or other construction operations are to be performed or otherwise shown on Drawings.

#### Protect tops, trunks, and roots of existing trees that are to remain on the site.

#### Clear areas and dispose of other trees, brush and vegetation before starting construction.

#### Remove tree stumps and roots larger than three inches in diameter and backfill resulting excavations with approved material.

### Stripping:  The CONTRACTOR shall remove topsoil from areas within limits of excavation and areas designated to receive backfill compaction as shown on the Drawings, required and as provided below:

Scrape area clean of all brush, grass, weeds, roots, and other material.

#### Strip to depth of approximately six inches or to a sufficient depth to remove excessive roots in heavy vegetation or brush areas and as required segregating topsoil.

#### Stockpile topsoil in areas where it will not interfere with construction operations or existing facilities.  Stockpiled topsoil shall be reasonably free of subsoil, debris and stones larger than two inches in diameter.

## 3-02	DISPOSAL OF SURPLUS AND UNSUITABLE MATERIAL:

## A.	The CONTRACTOR shall dispose of all excess or excavated material off-site or in areas otherwise approved by the OWNER.

## 3-03	STOCKPILE OF EXCAVATED MATERIAL:

## A.	The CONTRACTOR may temporarily stockpile excavated materials in areas shown in areas approved by the ENGINEER. Contractor shall not stockpile any materials on service bridge, concrete apron slab access roads and parking areas. All stockpile shall be no closer than 15 feet from any canal bank line or other improvements. All excavated materials not reused shall be removed from work site; or, if permission is granted by OWNER, place fill according to OWNER’s direction.

## 3-04	PLACEMENT OF BACKFILL:

## A.	The CONTRACTOR shall place all types of clay type soil backfill true to the lines, grades and cross sections shown in the Drawings or as ordered by the ENGINEER.  No.2 Stone granular backfill shall be deposited by the CONTRACTOR in horizontal layers not exceeding eight inches in depth measured loose and shall be compacted to a density of not less than 90 percent of the maximum density as determined by ASTM Standards.

## 3-06	GRADING:

## A.	The CONTRACTOR shall perform grading of the backfilled areas provided for below:

### 1.	Grade and compact all areas within the project area, including excavated and filled sections and adjacent transition areas, reasonably smooth, and free from irregular surface changes.

### 2.	Degree of finish shall be that ordinarily obtained from blade grader or scraper operations except as otherwise specified.

## 3-07	CLEANUP:

## A.	The CONTRACTOR shall cleanup the site as required and provided for below:

### 1.	Clear surfaces of all loose stones, roots, grading stakes and other objectionable materials.

2.	Keep paved areas clean and promptly remove rock or dirt dropped upon surfaces.

3-08	PROTECTION AND MAINTENANCE:

## A.	The CONTRACTOR shall maintain the backfill surfaces until acceptance of all backfill work. The maintenance shall include repairs of any erosion, slides, ruts or other damages. All new soil surfaces shall be seeded or sodded by Contractor upon completion of work using centipede or other approved seeds. Contractor shall water soil weekly to insure grass proper growth for a minimum of 2 months.

## PART 4 – MEASUREMENT AND PAYMENT

4-01	MEASUREMENT AND PAYMENT:

Payment for excavation and soil backfill shall include furnishing all plant labor, materials and equipment needed to excavate and backfill to grades on Drawings and dispose of excavated materials from work site.

A.	There will be no measurement for payment for excavation work.  Payment for excavation work will be made at the contract lump sum price under Item No. X-xxx “General Excavation”.

B.	Measurement for payment for soil placed as backfill will be based on the Ton and measured by Engineer approved truck weight tickets.

C.	There will be no direct payment for grass seeds, placement, and watering. Payment for grass planting work will be made at the contract lump sum price under Item No. X-xxx “General Excavation”.

***END OF SECTION***