SECTION 03100

CONCRETE FORMWORK AND ACCESSORIES

# GENERAL

## 1-01	SCOPE:

### The CONTRACTOR shall provide all labor, materials and equipment for the following:

#### Design and construction of all necessary formwork including the required bracing, supports, scaffolding, shoring, and other false work to produce cast-in-place concrete in the finished structure within the required tolerances for line, grade dimension and detail.

#### Joints in concrete, complete and in place, in accordance with the Contract Documents.  Joints in concrete structures shall be the types defined below and will be permitted only where indicated, unless specifically accepted by the ENGINEER.

B.	Related work specified elsewhere:

#### 1.	SECTION 03300 Cast-in-Place Concrete.

#### 2.	SECTION 07900 Sealants.

## 1-02	APPLICABLE PUBLICATIONS:

## A.	The following standard specifications shall apply to the work of this section:

### 1.	American Concrete Institute (ACI)

#### a.	ACI 347 - Recommended Practice for Concrete Formwork,

#### b.	ACI 117 - Standard Tolerances for Concrete Construction and Materials

### 2.	American Society of Testing and Materials (ASTM)

#### a.	A 775 - Epoxy Coated Reinforcing Steel Bars

#### b.	C 920 - Elastomeric Joint Sealant

#### c.	D 412 - Standard Test Method for Vulcanized Rubber and Thermoplastic Elastomers - Tension

#### d.	D 624 - Standard Test Method for Tear Strength of Conventional Vulcanized Rubber and Thermoplastic Elastomers

#### e.	D 638 - Standard Test Method for Tensile Properties of Plastics

#### f.	D 746 - Standard Test Method for Brittleness Temperature of Plastics and Elastomers by Impact

#### g.	D 747 - Standard Test Method for Apparent Bending Modulus of Plastics by Means of a Cantilever Beam

#### h.	D 1056 - Flexible Cellular Materials - Sponge or Expanded Rubber

#### i.	D 1752 - Preformed Sponge Rubber and Cork Expansion Joint Fillers for Concrete Paving and Structural Construction

#### j.	D 2000 - Standard Classification System for Rubber Products in Automotive Applications

#### k.	D 2240 - Standard Test Method for Rubber Property - Durometer Hardness

#### l.	D 2241 - Poly (Vinyl Chloride) (PVC) Pressure-Rated Pipe (SDR Series)

### 3.	US Product Standards (PS)

#### a.	PS-1 - Construction and Industrial Plywood, for Concrete Forms

#### b.	PS-20 - American Softwood Lumber Standard

### 4.	NSF International

#### a.	NSF 61 - Drinking Water System Components - Health Effects

### 5.	United States Army Corps of Engineers (USACE)

#### a.	CRD-C572 - PVC Waterstops

### 6.	Federal Specifications

#### a.	TT-S-0227 E(3) - Sealing Compound, Elastomeric Type, Multicomponent, for Caulking, Sealing, and Glazing Buildings and Other Structures

### 7.	Occupational Safety and Health Association (OSHA)

#### a.	CFR Title 29 Part 1926 - Safety and Health Regulations for Construction

## 1-03	DEFINITIONS:

### A.	Construction Joints:

#### 1.	When fresh concrete is placed against a hardened concrete surface, the joint between the two pours is called a construction joint.  If indicated on the drawings, joints in water bearing members shall be provided with a waterstop and/or sealant groove of the shape indicated.  The surface of the first pour may also be required to receive a coating of bond breaker as indicated.

### B.	Contraction Joints:

#### 1.	Contraction joints are similar to construction joints except that the fresh concrete shall not bond to the hardened surface of the earlier pour, which shall be coated with a bond breaker.  The slab reinforcement shall be stopped 4-1/2 inches from the joint, which is provided with a sleeve-type dowel, to allow shrinkage of the concrete of the later pour.  Waterstop and/or sealant groove shall also be provided when indicated.

#### C.	Expansion Joints:

#### 1.	To allow the concrete to expand freely, a space is provided between the two pours, and the joint shall be formed as indicated.  The space is obtained by placing a filler joint material against the earlier pour, to act as a form for the later pour.  Unless otherwise indicated, expansion joints in water bearing members shall be provided with a center-bulb type waterstop as indicated.

#### 2.	Premolded expansion joint material shall be installed with the edge at the indicated distance below or back from finished concrete surface, and shall have a slightly tapered, dressed, and oiled wood strip secured to or placed at the edge thereof during concrete placement, which shall later be removed to form space for sealing material.

#### The space so formed shall be filled with a joint sealant material as indicated herein.  In order to keep the two walls or slab elements in line the joint shall also be provided with a sleeve-type dowel as indicated.

### D.	Control Joints:

#### 1.	The function of the control joint is to provide a weaker plane in the concrete, where shrinkage cracks will probably occur.  A groove, of the shape and dimensions indicated, is formed or saw-cut in the concrete.  This groove is afterward filled with a joint sealant material.

## 1-04	SUBMITTALS:

### A.	Falsework Calculations and Drawings: The Contractor shall submit calculations and drawings prepared and sealed by a Professional Civil Engineer registered in State of Louisiana, which indicate the falsework complies with the requirements of OSHA Title 29, Part 1926.703.  The submission of design details and calculations for falsework is for information only.

### B.	The plans of falsework proposed to be used shall be in sufficient detail to indicate the general layout, sizes of members, anticipated stresses, grade of materials to be used in the falsework, means of protecting existing construction which supports falsework, and typical soil conditions.

### C.	The CONTRACTOR shall submit placement drawings showing the location and type of all joints for each structure.

### D.	All Submittals shall have the original and three (3) copies sent 60 days prior to start of work.

### E.	The CONTRACTOR shall submit Manufacturer’s information demonstrating compliance with requirements for the following:

#### 1.	Form ties and related accessories, including taper tie plugs, if taper ties are used.

#### 2.	Form gaskets.

#### 3.	Form release agent, including NSF certification if not using mineral oil.

#### List of form materials and locations for use.

#### Bearing Pads

#### Neoprene Sponge

#### Preformed Joint Filler

#### Backing Rod

#### Bond Breaker

#### Waterstops

#### Slip Dowels

#### PVC Tubing

## 1-05	RESPONSIBILITIES:

### A.	The CONTRACTOR is fully responsible for the design and construction of all forms and falsework to be in compliance with all applicable OSHA requirements, and the requirements of all agencies having jurisdiction on the project.  The submission of design details and calculations for falsework is for information only.

### B.	The sealant material shall show no signs of adhesive or cohesive failure when tested in accordance with the following procedure in laboratory and field tests:

#### 1.	Sealant specimen shall be prepared between 2 concrete blocks (1-inch by 2-inch by 3-inch).  Spacing between the blocks shall be 1-inch.  Coated spacers (2-inch by 1-1/2-inch by 1/2-inch) shall be used to insure sealant cross-sections of 1/2-inch by 2 inches with a width of 1-inch.

#### 2.	Sealant shall be cast and cured according to manufacturer's recommendations except that curing period shall be not less than 24 hours.

#### 3.	Following curing period, the gap between blocks shall be widened to 1-1/2-inch.  Spacers shall be used to maintain this gap for 24 hours prior to inspection for failure.

## 1-06	CERTIFICATIONS:

### A.	Form materials, which may remain or leave residues on or in the concrete, shall be certified as compliant with NSF 61.

### B.	Joint materials shall be certified as compliant with NSF 61.

### C.	CONTRACTOR shall submit certified test reports from the sealant manufacturer on the actual batch of material being supplied indicating compliance with requirements herein before the sealant is used on the job.

### D.	CONTRACTOR is to provide copies of the Waterstop Welding Certifications provided by manufacturer or authorized agent of manufacturer for every person who is to be involved with waterstop installation.

## 1-07	INSPECTIONS:

### A.	Falsework shall be inspected for conformance with the accepted submittal.  No workers will be allowed to use falsework for access and no concrete placement to related forms will be permitted until the falsework is inspected by the CONTRACTOR for conformance with the submittals and appropriately tagged.  No variations or alterations to falsework, as compared to the reference submittal, will be allowed without certification of the variation by the original Professional Engineer.

### B.	All waterstop field joints shall be subject to rigid inspection, and no such WORK shall be scheduled or started without having made prior arrangements with the ENGINEER for the required inspections.  Not less than 24 hours notice shall be given for scheduling such inspections.

### C.	Field joints in waterstops shall be subject to rigid inspection for misalignment, bubbles, inadequate bond, porosity, cracks, offsets, and other defects, which would reduce the potential resistance of the material to water pressure at any point.  Defective joints shall be replaced with material, which passes inspection; faulty material shall be removed from the site and properly disposed of.

### D.	The following waterstop defects represent a partial list of defects which shall be grounds for rejection:

#### 1.	Offsets at joints greater than 1/16-inch or 15 percent of material thickness, at any point, whichever is less.

#### 2.	Exterior crack at joint, due to incomplete bond, which is deeper than 1/16-inch or 15 percent of material thickness, at any point, whichever is less.

#### 3.	Any combination of offset or exterior crack which will result in a net reduction in the cross section of the waterstop in excess of 1/16-inch or 15 percent of material thickness at any point, whichever is less.

#### 4.	Misalignment of joint which results in misalignment of the waterstop in excess of 1/2-inch in 10 feet.

#### 5.	Porosity in the welded joint as evidenced by visual inspection.

#### 6.	Bubbles or inadequate bonding which can be detected with a penknife test.  (If, while prodding the entire joint with the point of a penknife, the knife breaks through the outer portion of the weld into a bubble, the joint shall be considered defective.)

#### 7.	Visible signs of separation when the cooled splice is bent by hand at any sharp angle.

#### 8.	Any evidence of burned material.

## 1-08	WARRANTY:

### A.	The CONTRACTOR shall furnish a 5-year written warranty of the entire sealant installation against faulty and/or incompatible materials and workmanship, together with a statement that it agrees to repair or replace, to the satisfaction of the ENGINEER, any such defective areas which become evident within said 5-year guarantee period.

# PRODUCTS

## 2-01	FORM AND FALSEWORK MATERIALS:

### Except as otherwise expressly accepted by the ENGINEER, lumber brought on the Site for use as forms, shoring, or bracing shall be new material.  Forms shall be smooth surface forms and shall be of the following materials:

Walls	-	Steel, fiberglass, or plywood panel

Columns	-	Steel, plywood, PVC, fiberglass, or spiral wound fiber forms

Roof and floor	-	Plywood

All other work	- 	Steel panels, fiberglass, or plywood

### Materials for concrete forms, formwork, and falsework shall conform to the following requirements:

#### Plywood shall be new, waterproof, synthetic resin bonded, exterior type, manufactured especially for concrete formwork and shall conform to Plyform Class I, B-B EXT, of PS-1, and shall be edge sealed.

#### Lumber shall be Douglas Fir or Southern Yellow Pine, construction grade or better, in conformance with PS 20.

#### Form materials shall be metal, wood, plywood, or other material that will not adversely affect the concrete and will facilitate placement of concrete to the shape, form, line, and grade indicated.  Metal forms shall accomplish such results.  Wood forms for surfaces to be painted shall be Medium Density Overlaid plywood, MDO EXT Grade.

### Unless otherwise indicated, exterior corners in concrete members shall be provided with 3/4-inch chamfers.  Re-entrant corners in concrete members shall not have fillets unless otherwise indicated.

### Forms and falsework to support the roof and floor slabs shall be designed in accordance with ACI 347.

## 2-02	FORM TIES:

### A.	Ties shall be standard crimped snap ties with one-inch (1”) snapback.  Ties shall be provided with a plastic cone or other suitable means for forming a conical hole to insure that the form tie may be broken off back of the face of the concrete.  The maximum diameter of removable cones for rod ties, or of other removable form-tie fasteners having a circular cross-section, shall not exceed 1-1/2 inches; and all such fasteners shall be such as to leave holes of regular shape for reaming.  Form ties for water-retaining structures shall have integral waterstops that tightly fit the form tie so that they cannot be moved from mid-point of the tie.

### B.	Removable taper ties may be used when approved by the ENGINEER.  A preformed neoprene or polyurethane tapered plug sized to seat at the center of the wall shall be inserted in the hole left by the removal of the taper tie.

## 2-03	FORM RELEASING AGENT:

### A.	Form release agent shall be non-staining and shall leave no residues on or in the concrete unless certified as compliant with NSF 61 and shall not adversely affect the adhesion of paint or other coatings.

## 2-04	WATERSTOPS:

### A.	PVC Waterstops:

#### PVC Waterstops shall be extruded from an elastomeric polyvinyl chloride compound containing the plasticizers, resins, stabilizers, and other materials necessary to meet the requirements of this Section.  No reclaimed or scrap material shall be used.  The CONTRACTOR shall obtain from the waterstop manufacturer and shall furnish to the ENGINEER for review, current test reports and a written certification of the manufacturer that the material to be shipped to the job meets the physical requirements as outlined in the USACE CRD-C572, and those listed herein.

#### Flatstrip and Center-Bulb Waterstops:  The thickness of waterstops, including the center bulb, shall not be less than 3/8-inch.  Waterstop shall be provided with factory installed hog rings at 12 inches on centers along the waterstop.

#### Multi-Rib Waterstops:  Multi-rib waterstops where required shall have prefabricated (shop made fitting) joint fittings at all intersections of the ribbed-type waterstops.

#### Retrofit Waterstops:  Retrofit waterstops and batten bars shall be manufactured as a complete system including waterstop, SS batten bar, SS anchor bolts, and epoxy gel.

#### Waterstop Testing Requirements:  When tested in accordance with the test standards, the waterstop material shall meet or exceed the following requirements:

| Property | Value | ASTM Standard |
| --- | --- | --- |
| Physical Property, Sheet Material |  |  |
| Tensile Strength-min (psi) | 2000 | D 638, Type IV |
| Ultimate Elongation-min (percent) | 350 | D 638, Type IV |
| Low Temp Brittleness-max (degrees F) | -35 | D 746 |
| Stiffness in Flexure-min (psi) | 600 | D 747 |
| Accelerated Extraction (CRD-C572) |  |  |
| Tensile Strength-min (psi) | 1500 | D 638, Type IV |
| Ultimate Elongation-min (percent) | 300 | D 638, Type IV |
| Effect of Alkalies (CRD-C572) |  |  |
| Change in Weight (percent) | + 0.25/- 0.10 | ------ |
| Change in Durometer, Shore A | +/- 5 | D 2240 |
| Finish Waterstop |  |  |
| Tensile Strength-min (psi) | 1400 | D 638, Type IV |
| Ultimate Elongation-min (percent) | 280 | D 638, Type IV |

### B.	Pre-formed Hydrophilic Waterstops:

#### 1.	Hydrophilic (bentonite-free) waterstops shall be the type that expands in the presence of water to form a watertight joint seal without damaging the concrete in which it is cast.

#### 2.	Waterstop shall be manufactured from chloroprene rubber and modified chloroprene rubber with hydrophilic properties.  Waterstop shall have a delay coating to inhibit initial expansion due to moisture present in fresh concrete.  The minimum expansion ratio of modified chloroprene shall be not less than 2 to 1 volumetric change in distilled water at 70 degrees F (21 degrees C).

#### 3.	Hydrophilic Waterstop shall meet the following minimum requirements:

| Property | Value | ASTM Standard |
| --- | --- | --- |
| Physical Property, Chloroprene |  |  |
| Tensile Strength-min (psi) | 1275 | D 412 |
| Ultimate Elongation-min (percent) | 350 | D 412 |
| Hardness, Shore A | 55 +/- 5 | D 2240 |
| Physical Property, Modified Chloroprene |  |  |
| Tensile Strength-min (psi) | 300 | D 412 |
| Ultimate Elongation-min (percent) | 600 | D 412 |
| Hardness, Shore A | 55 +/- 5 | D 2240 |

#### 4.	Bonding agent for hydrophilic waterstop shall be the manufacturer's recommended adhesive for wet, rough concrete.

### C.	Other Types of Waterstops:

#### 1.	When types of waterstops not listed above are indicated, they shall be subjected to the same requirements as those listed herein.

## 2-05	JOINT SEALANT FOR WATER BEARING JOINTS:

### A.	Joint sealant shall be polyurethane polymer designed for bonding to concrete, which is continuously submerged in water.  No material will be acceptable which has an unsatisfactory history as to bond or durability when used in the joints of water retaining structures.

### B.	Joint sealant material shall meet the following requirements  (73 degrees F and five percent R.H.):

| Requirement | Value | ASTM Standard |
| --- | --- | --- |
| Work Life (minutes) | 45 - 180 | ----- |
| Time to Reach 20 Shore "A" Hardness (at 77 degrees F, 200 gr quantity) - max (hours) | 24 | ----- |
| Ultimate Hardness | 20 - 45 Shore "A" | D 2240 |
| Tensile Strength - min (psi) | 175 | D 412 |
| Ultimate Elongation - min (percent) | 400 | D 412 |
| Tear Resistance - min (pounds per inch of thickness) | 75 | D 624 (Die C) |
| Color | Light Gray | ----- |

### C.	Polyurethane sealants for waterstop joints in concrete shall conform to the following requirements:

#### 1.	Sealant shall be 2-part polyurethane with the physical properties of the cured sealant conforming to or exceeding the requirements of ASTM C 920, or TT-S-0227 E (3) for 2-part material, as applicable.

#### 2.	For vertical joints and overhead horizontal joints, only "non-sag" compounds shall be used; all such compounds shall conform to the requirements of ASTM C 920 Class 25, Grade NS, or TT-S-0227 E(3), Type II, Class A.

#### 3.	For plane horizontal joints, the self-leveling compounds which meet the requirements of ASTM C 920 Class 25, Grade P, or TT-S-0227 E(3), Type I shall be used.  For joints subject to either pedestrian or vehicular traffic, a compound providing non-tracking characteristics, and having a Shore "A" hardness range of 35 to 45, shall be used.

#### 4.	Primer materials, if recommended by the sealant manufacturer, shall conform to the printed recommendations of the manufacturer.

### D.	Sealants for non-waterstop joints in concrete shall conform to Section 07920 - Sealants and Caulking.

## 2-06	JOINT MATERIALS:

### A.	Bearing Pad: Bearing pad shall be neoprene conforming to ASTM D 2000, BC 420, 40 durometer hardness unless otherwise indicated.

### B.	Neoprene Sponge: Sponge shall be neoprene, closed-cell, expanded, conforming to ASTM D 1056, Type 2C5-E1.

### C.	Joint Filler

#### 1.	Joint filler for expansion joints in waterholding structures shall be neoprene conforming to ASTM D1056, Type 2C5-E1.

#### 2.	Joint filler material in other locations shall be of the preformed non-extruding type joint filler constructed of cellular neoprene sponge rubber or polyurethane of firm texture.  Bituminous fiber type will not be permitted.  All non-extruding and resilient-type preformed expansion joint fillers shall conform to the requirements and tests set forth in ASTM D 1752, for Type I, except as otherwise indicated.

## 2-07	BACKING ROD:

### A.	Backing rod shall be an extruded closed-cell, polyethylene foam rod.  The material shall be compatible with the joint sealant material and shall have a tensile strength of not less than 40 psi and a compression deflection of approximately 25 percent at eight (8) psi.  The rod shall be 1/8-inch larger in diameter than the joint width except that a one-inch diameter rod shall be used for a 3/4-inch wide joint.

## 2-08	BOND BREAKER:

### A.	Bond breaker shall contain a fugitive dye so that areas of application will be readily distinguishable.

### B.	Bonding agent for hydrophilic waterstop shall be the manufacturer's recommended adhesive for wet, rough concrete.

## 2-09	SLIP DOWELS:

### A.	Slip dowels in joints shall be smooth epoxy-coated bars, conforming to ASTM A 775.

## 2-10	PVC TUBING:

### A.	PVC tubing in joints shall be Schedule SDR 13.5, conforming to ASTM D 2241.

## 2.11	CHAMFER STRIP:

### A.	Provide three quarter inch triangular fillets, milled clear straight grained wood, surfaced each side, or extruded vinyl type, with or without nail flange to form all exposed concrete edges such as columns, pilasters, beams, curbs, equipment pads, tops of walls, and as indicated.  Unless otherwise indicated, exterior corners in concrete members shall be provided with 3/4” chamfers.  Re-entrant corners in concrete members shall not have fillets, unless otherwise indicated.

# EXECUTION

## 3-01	FORMS:

### Forms shall conform to the shape, lines, and dimensions as shown on the Drawings and shall be substantial and sufficiently tight to prevent leakage.  Forms shall be properly braced or tied so as to maintain position and shape.  Plumb and string lines shall be installed before concrete placement and shall be maintained during placement.  Such lines shall be used by CONTRACTOR's personnel and by the ENGINEER and shall be in sufficient number and properly installed.  During concrete placement, the CONTRACTOR shall continually monitor plumb and string line form positions and immediately correct deficiencies.

### The CONTRACTOR shall be fully responsible for the adequacy of the formwork in its entirety and any forms that are unsafe or inadequate in any respect shall promptly be removed from the WORK and replaced. The CONTRACTOR shall provide worker protection from protruding reinforcement bars in accordance with applicable safety codes.

### CONTRACTOR may reuse forms only if in good condition and only if acceptable to the ENGINEER.  Reused forms shall be thoroughly cleaned and may require light sanding between uses to obtain a uniform surface texture on all exposed concrete surfaces.  Forms shall not be reused if they have developed defects that would affect the surface texture of exposed concrete.  Exposed concrete surfaces are defined as surfaces, which are permanently exposed to view.  In the case of forms for the inside wall surfaces of hydraulic/water retaining structures, unused tie rod holes in forms shall be covered with metal caps or shall be filled by other methods acceptable to the ENGINEER

### Forms shall be sufficiently tight to prevent leakage.  Forms shall be properly braced or tied together to maintain their position and shape under a load of freshly-placed concrete.  If adequate foundation for shores cannot be secured, trussed supports shall be provided.

### Immediately before the placing of reinforcing, faces of all forms in contact with concrete shall receive a thorough coating of form release agent.  Any excess agent shall be satisfactorily removed before placing concrete.  If using mineral oil, the CONTRACTOR shall oil the forms at least two weeks in advance of their use.  Care shall be exercised to keep oil/release agent off the surfaces of steel reinforcement and other items to be embedded in concrete.

### The CONTRACTOR shall supply sufficient number of forms of each kind to permit the required rate of progress to be maintained.

### The design and inspection of concrete forms, falsework, and shoring shall comply with applicable local, state, and Federal regulations.

## 3-02	WATERSTOPS:

### A.	Waterstops shall be embedded in the concrete across joints as indicated.  Waterstops shall be fully continuous for the extent of the joint.  Splices necessary to provide such continuity shall be accomplished in conformance to printed instructions of manufacturer of the waterstops.  The CONTRACTOR shall take suitable precautions and means to support and protect the waterstops during the progress of the work and shall repair or replace at its own expense any waterstops damaged during the progress of the work.  Waterstops shall be stored so as to permit free circulation of air around the waterstop material.

### B.	When any waterstop is installed in the concrete on one side of a joint, while the other half or portion of the waterstop remains exposed to the atmosphere for more than 2 days, suitable precautions shall be taken to shade and protect the exposed waterstop from direct rays of the sun during the entire exposure and until the exposed portion of the waterstop is embedded in concrete.

## 3-03	SPLICES IN PVC WATERSTOPS:

### A.	Splices in PVC waterstops shall be performed by heat sealing the adjacent waterstop sections in accordance with the manufacturer's printed recommendations.  It is essential that:

#### The material not be damaged by heat sealing.

#### The splices have a tensile strength of not less than 80 percent of the unspliced material tensile strength.

#### The continuity of the waterstop ribs and of its tubular center axis be maintained. No edge welding is allowed.

### B.	Butt joints of the ends of 2 identical waterstop sections may be made while the material is in the forms.

### C.	All joints with waterstops involving more than 2 ends to be jointed together, and all joints which involve an angle cut, alignment change, or the joining of 2 dissimilar waterstop sections shall be prefabricated (shop made fitting) prior to placement in the forms, allowing not less than 24-inch long strips of waterstop material beyond the joint.  Upon being inspected and approved, such prefabricated (shop made fitting) waterstop joint assemblies shall be installed in the forms and the ends of the 24-inch strips shall be butt welded to the straight run portions of waterstop in place in the forms.

### D.	Where a centerbulb waterstop intersects and is jointed with a non-centerbulb waterstop, care shall be taken to seal the end of the centerbulb, using additional PVC material if needed.

## 3-04	FORM DESIGN:

### A.	Forms shall be true in every respect to the required shape and size, shall conform to the established alignment and grade, and shall be of sufficient strength and rigidity to maintain their position and shape under the loads and operations incident to placing and vibrating the concrete.  Suitable and effective means shall be provided on all forms for holding adjacent edges and ends of panels and sections tightly together and in accurate alignment so as to prevent the formation of ridges, fins, offsets, or similar surface defects in the finished concrete.

### B.	Plywood, 5/8-inch and greater in thickness, may be fastened directly to studding if the studs are spaced close enough to prevent visible deflection marks in the concrete.  The forms shall be tight so as to prevent the loss of water, cement, and fines during placing and vibrating of the concrete.  Specifically, the bottom of wall forms that rest on concrete footings or slabs shall be provided with a gasket to prevent loss of fines and paste during placement and vibration of concrete.  Such gasket may be a 1- to 1-1/2-inch diameter polyethylene rod held in position to the underside of the wall form.

### C.	The CONTRACTOR shall provide adequate clean-out holes at the bottom of each lift of forms.  The size, number, and location of such clean-outs shall be as acceptable to the ENGINEER.  Whenever concrete cannot be placed from the top of a wall form in a manner that meets the requirements of the Contract Documents, form windows shall be provided in the size and spacing needed to allow placement of concrete to the requirements of SECTION 03300 Cast-in-Place Concrete.  The size, number, and location of such form windows shall be as acceptable to the ENGINEER.

## 3.05	FORM CONSTRUCTION:

### A.	Vertical Surfaces:  All vertical surfaces of concrete members shall be formed, except where placement of the concrete against the ground is indicated.  Not less than 1-inch of concrete shall be added to the indicated thickness of a concrete member, where concrete is permitted to be placed against trimmed ground, in lieu of forms.  Permission to do this on other concrete members will be granted only for members of comparatively limited height and where the character of the ground is such that it can be trimmed to the required lines and will stand securely without caving or sloughing until the concrete has been placed.

### B.	Construction Joints:  Concrete construction joints will not be permitted at locations other than those indicated, except as may be acceptable to the ENGINEER.  When a second lift is placed on hardened concrete, special precautions shall be taken in the way of the number, location, and tightening of ties at the top of the old lift and bottom of the new to prevent any unsatisfactory affect whatsoever on the concrete.  Pipe stubs and anchor bolts shall be set in the forms where required.

### C.	Form Ties

#### 1.	Embedded Ties:  Holes left by the removal of form tie cones shall be reamed with suitable toothed reamers so as to leave the surface of the holes clean and rough before being filled with mortar.  Wire ties for holding forms will not be permitted.  No form-tying device or part thereof, other than metal, shall be left embedded in the concrete.  Ties shall not be removed in such manner as to leave a hole extending through the interior of the concrete members.  The use of snap-ties, which cause spalling of the concrete upon form stripping or tie removal, will not be permitted.  If steel panel forms are used, rubber grommets shall be provided where the ties pass through the form in order to prevent loss of cement paste.  Where metal rods extending through the concrete are used to support or to strengthen forms, the rods shall remain embedded and shall terminate not less than 1-inch back from the formed face or faces of the concrete.

#### 2.	Removable Ties:  Where taper ties are approved for use, the larger end of the taper tie shall be on the wet side of walls in water retaining structures.  After the taper tie is removed, the hole shall be thoroughly cleaned and roughened for bond.  A precast neoprene or polyurethane tapered plug shall be located at the wall centerline.  The hole shall be completely filled with non-shrink grout for water bearing and below-grade walls.  The hole shall be completely filled with non-shrink or regular cement grout for above-grade walls, which are dry on both sides.  Exposed faces of walls shall have the outer 2 inches of the exposed face filled with a cement grout, which shall match the color and texture of the surrounding wall surface.

## 3-06	JOINT CONSTRUCTION:

### A.	Setting Waterstops:

#### 1.	In order to eliminate faulty installation that may result in joint leakage, the CONTRACTOR shall be particularly careful to get the correct positioning of the waterstops during installation.  Adequate provisions must be made to support and anchor the waterstops during the progress of the WORK and to insure the proper embedment in the concrete.  The symmetrical halves of the waterstops shall be equally divided between the concrete pours at the joints.  The center axis of the waterstops shall be coincident with the joint openings.  Maximum density and imperviousness of the concrete shall be insured by thoroughly working it in the vicinity of all joints.

#### 2.	In placing PVC waterstops in the forms, the CONTRACTOR shall provide means to prevent the waterstop from being folded over by the concrete as it is placed.  Waterstops shall be held in place with light wire ties on 12-inch centers which shall be passed through hog rings at the edge of the waterstop and tied to the curtain of reinforcing steel.  Horizontal waterstops, with their flat face in a vertical plane, shall be held in place with continuous supports to which the top edge of the waterstop shall be tacked.  In placing concrete around horizontal waterstops, with their flat face in a horizontal plane, the CONTRACTOR shall work concrete under the waterstops by hand so as to avoid the formation of air and rock pockets.

#### 3.	In placing centerbulb waterstops in expansion joints, the centerbulb shall be centered on the joint filler material.

#### Waterstop in vertical wall joints shall stop 6 inches from the top of the wall where such waterstop does not connect with any other waterstop and is not to be connected to a future concrete placement.

### B.	Joint Location:

#### 1.	Construction joints and other types of joints shall be provided where indicated.  When not indicated, construction joints shall be provided at 25-foot maximum spacing for all concrete construction.  Where joints are indicated spaced greater than 40 feet apart, additional joints shall be provided to maintain the 25-foot maximum spacing.  The location of all joints, of any type, shall be submitted for acceptance by the ENGINEER.

### C.	Joint Preparation:

#### 1.	The CONTRACTOR shall take special care in preparing concrete surfaces at joints where bonding between 2 sections of concrete is required.  Unless otherwise indicated, such bonding will be required at all horizontal joints in walls.  Surfaces shall be prepared in accordance with the requirements of SECTION 03300 Cast-in-Place Concrete.  Except on horizontal wall construction joints, wall to slab joints, or where otherwise indicated, at all joints where waterstops are required, the joint face of the first pour shall be coated with a bond breaker as indicated herein.

### D.	Retrofit Joint Preparation:

#### 1.	Existing surfaces to receive a retrofit waterstop shall be clean and free from any loose or foreign material.  Surface shall be given a light sandblast or hydroblast finish to 1/8-inch amplitude prior to application of epoxy and waterstop.

### E.	Construction Joint Sealant:

#### 1.	Construction joints in water-bearing floor slabs, and elsewhere as indicated, shall be provided with tapered grooves which shall be filled with a construction joint sealant.  The material used for forming the tapered grooves shall be left in the grooves until just before the grooves are cleaned and filled with joint sealant.  After removing the forms from the grooves, all laitance and fins shall be removed, and the grooves shall be sandblasted.  The grooves shall be allowed to become thoroughly dry, after which they shall be blown out; immediately thereafter, they shall be primed, bond breaker tape placed in the bottom of the groove, and filled with the construction joint sealant.  The primer shall be furnished by the sealant manufacturer.  No sealant will be permitted to be used without a primer.  Care shall be used to completely fill the sealant grooves.  Areas designated to receive a sealant fillet shall be thoroughly cleaned, as outlined for the tapered grooves, prior to application of the sealant.

#### 2.	The primer and sealant shall be placed strictly in accordance with the printed recommendations of the manufacturer, taking special care to properly mix the sealant prior to application.  The sides of the sealant groove shall not be coated with bond breaker, curing compound, or any other substance which would interfere with proper bonding of the sealant.  Sealant shall achieve final cure at least 7 days before the structure is filled with water.

#### 3.	Sealant shall be installed by a competent waterproofing specialty contractor who has a successful record of performance in similar installations.

#### 4.	Thorough, uniform mixing of 2-part, catalyst-cured materials is essential; special care shall be taken to properly mix the sealer before its application.  Before any sealer is placed, the CONTRACTOR shall arrange to have the crew doing the WORK carefully instructed on the proper method of mixing and application by a representative of the sealant manufacturer.

#### Any joint sealant which fails to fully and properly cure after the manufacturer's recommended curing time for the conditions of the WORK hereunder shall be completely removed; the groove shall be thoroughly sandblasted to remove all traces of the uncured or partially cured sealant and primer, and shall be re-sealed with the indicated joint sealant.  Costs of such removal, joint treatment, re-sealing, and appurtenant work shall be the CONTRACTOR’s responsibility.

### F.	Hydrophilic Waterstop

#### 1.	Where a hydrophilic waterstop is called for in the Contract Documents, it shall be installed with the manufacturer's instructions and recommendations except as modified herein.

#### 2.	When requested by the ENGINEER, the CONTRACTOR shall arrange for the manufacturer to furnish technical assistance in the field.

#### 3.	Hydrophilic waterstop shall only be used where complete confinement by concrete is provided. Hydrophilic waterstop shall not be used in expansion or contraction joints or in the first 6 inches of any non-intersecting joint.

#### 4.	The hydrophilic waterstop shall be located as near as possible to the center of the joint and it shall be continuous around the entire joint.  The minimum distance from the edge of the waterstop to the face of the member shall be 5 inches.

#### 5.	Where the thickness of the concrete member to be placed on the hydrophilic waterstop is less than 12 inches, the waterstop shall be placed in grooves formed or ground into the concrete.  The groove shall be at least 3/4 inch deep and 1-1/4 inches wide.  When placed in the groove, the minimum distance from the edge of the waterstop to the face of the member shall be 2.5 inches.

#### Where a hydrophilic waterstop is used in combination with PVC waterstop, the hydrophilic waterstop shall overlap the PVC waterstop for a minimum of 6 inches and shall be adhered to PVC waterstop with single component water-swelling sealant as recommended by manufacturer.

#### The hydrophilic waterstop shall not be installed where the air temperature falls outside the manufacturer's recommended range.

#### The concrete surface under the hydrophilic waterstop shall be smooth and uniform.  The concrete shall be ground smooth if needed.  Alternately, the hydrophilic waterstop shall be bonded to the surface using an epoxy grout which completely fills all voids and irregularities beneath the waterstop material.  Prior to installation, the concrete surface shall be wire brushed to remove any laitance or other materials that may interfere with the bonding of epoxy.

#### The hydrophilic waterstop shall be secured in place with concrete nails and washers at 12-inch maximum spacing.  This shall be in addition to the adhesive recommended by the manufacturer.

### G.	Retrofit Waterstop:

#### 1.	Retrofit waterstops shall be set in a bed of epoxy over a sandblasted surface with stainless steel batten bars and 1/4-inch diameter stainless steel anchors at 6 inches on center, staggered, and in accordance with the manufacturer's written recommendations.

## 3-07	REMOVAL OF FORMS:

### A.	Careful procedures for the removal of forms shall be strictly followed, and this WORK shall be done with care so as to avoid injury to the concrete or workers.  In the case of roof slabs and above-ground floor slabs, forms shall remain in place until test cylinders for the roof concrete attain a minimum compressive strength of 75 percent of the 28-day strength (0.75f'c) in SECTION 03300.  No forms shall be disturbed or removed under an individual panel or unit before the concrete in all the adjacent panels or units have attained 0.75f'c strength and have been in place for a minimum of 7 days.  The time required to establish said strength shall be determined by the ENGINEER who will make several test cylinders for this purpose from concrete used in the first group of roof panels placed.  If the time so determined is more than the 7-day minimum, then that time shall be used as the minimum length of time. Forms for vertical walls of waterholding structures shall remain in place at least 36 hours after the concrete has been placed.

### B.	Forms for parts of the WORK not specifically mentioned herein shall remain in place for periods of time as recommended in ACI 347.

## 3-08	FALSEWORK:

### A.	The CONTRACTOR shall be responsible for the design, engineering, construction, maintenance, and safety of all falsework, including staging, walkways, forms, ladders, and similar appurtenances, which shall equal or exceed the applicable requirements of the provisions of the OSHA Safety and Health Standards for Construction, and the requirements herein.

### B.	The CONTRACTOR shall design and construct falsework to provide the necessary rigidity and to support the loads.  Falsework for the support of a superstructure shall be designed to support the loads that would be imposed if the entire superstructure were placed at one time.

### C.	The CONTRACTOR shall place falsework upon a solid footing, safe against undermining, and protected from softening.  When the falsework is supported on timber piles, the maximum calculated pile loading shall be as recommended by the CONTRACTOR’S geotechnical engineer and shall not exceed 20 tons.  When falsework is supported on any portion of the structure which is already constructed, the load imposed by the falsework shall be spread, distributed, and braced in such a way as to avoid any possibility of damage to the structure.

## 3-09	TOLERANCES:

### The variation from plumb, level and required lines shall not exceed 1/4-inch in any ten feet (10’) of length, non cumulative, and there shall be no offsets or visible waviness in the finished surface.  All other tolerances shall be within the tolerances of ACI 117 - Standard Tolerances for Concrete Construction and Materials.

***END OF SECTION***