# SECTION 16140

WIRING DEVICES

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS:

A.	Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specification sections, apply to work of this section.

B.	This section is a Division 16 Basic Materials and Methods section, and is part of each Division 16 section making reference to wiring devices specified herein.

1.02	DESCRIPTION OF WORK:

A.	The extent of wiring device is indicated by drawings and schedules.  Wiring devices are defined as single discrete units of electrical distribution systems, which are intended to carry but not utilize electric energy.

PART 2 - PRODUCTS

2.01	FABRICATED WIRING DEVICES:

A.	General:  Provide factory-fabricated wiring devices, in types, colors, and electrical ratings for applications indicated and complying with NEMA Stds. Pub. No. WD 1.  Where types and grades are not indicated, provide proper selection as determined by Installer to fulfill wiring requirements, and complying with NEC and NEMA standards for wiring devices.  Provide ivory color devices and wallplates except as indicated otherwise.  Color selection of devices and wallplates shall be verified by Contractor with the Engineer.  All devices of similar types shall be by the same manufacturer.

2.02.	RECEPTACLES:

A.	General:   Provide duplex “Corrosion Resistant Industrial Specification Grade” receptacles, all current carrying metal parts (contacts, terminals and screws) shall be corrosion resistant and nickel-coated, 2-pole 3-wire grounding, with green hexagonal equipment ground screw, ground terminals and poles internally connected to mounting yoke and mounting yoke provided with automatic grounding feature between mounting screws and yoke, 20 ampere 125-volts, with metal plaster ears, back and side wiring, yoke shall be one piece brass construction, receptacle face shall be heavy duty high impact nylon.  NEMA configuration 5-20R.  Do not use “stab-in” wiring method.

B.	Ground-Fault Interrupter:  Where indicated on drawings, provide duplex receptacles with ground-fault circuit interrupters (GFCI), UL-rated Class A, with solid-state ground-fault sensing and signaling, with 5 milliamperes ground-fault trip level, and with local test/reset buttons.

C.	Weather-Proof:  Where indicated on drawings, provide duplex receptacles that are listed as weather-resistant, installed in a weather-proof outlet box.  Receptacles shall remain wet location listed while in use.

2.03	SWITCHES:

A.	General:  All switches shall be industrial grade, provided with automatic grounding clip on mounting yoke; silver cadmium oxide contacts; neoprene bumper pads to cushion handle; one piece rivetless spring contact arm and terminal plate.

B.	Toggle: Provide quiet, AC-type, single-pole and 3-way toggle switches, 20-amperes, 120/277-volts AC, with mounting yoke insulated from mechanism; equip with plaster ears, switch handle, side-wired screw terminals and backwiring with clamp type terminals.

PART 3 - EXECUTION

3.01	INSTALLATION:

A.	Install wiring devices as indicated, in compliance with manufacturer’s written instructions, applicable requirements of NEC and NECA’s “Standard of Installation,” and in accordance with recognized industry practices to fulfill project requirements.

B.	Verify location of all devices with Engineer before beginning construction.

C.	Install wiring devices only in electrical boxes, which are clean, free from excess building materials, dirt and debris.

D.	Install weatherproof while-in-use covers at all damp or exposed locations, or as indicated on drawings.

E.	Tighten connectors and terminals, including screws and bolts, in accordance with equipment manufacturer’s published torque-tightening values for wiring devices.  Where manufacturer’s torquing requirements are not indicated, tighten connectors and terminals to comply with tightening torques specified in UL Stds. 486A and 486B.  Use properly scaled torque indicating hand tool.

3.04	GROUNDING:

A.	Provide electrically continuous, tight grounding connections for wiring devices, unless otherwise indicated.

3.05	TESTING:

A.	Prior to energizing circuitry, test wiring devices for electrical continuity and proper polarity connections.  After energizing circuitry, test wiring devices to demonstrate compliance with requirements.

## END SECTION -