# SUB-SECTION 16195

ELECTRICAL IDENTIFICATION

# PART 1 - GENERAL

1.01	RELATED DOCUMENTS:

A.		Drawings and general provisions of Contract, including General and Special Provisions and Division 1 Specifications sections, apply to work of this section.

B.		This section is a Division 16 Basic Materials and Methods section and is part of each Division 16 section making reference to electrical identification specified herein.

PART 2 - PRODUCTS

2.01	ELECTRICAL IDENTIFICATION MATERIALS:

A.		General: Except as otherwise indicated, provide manufacturer’s standard products of categories and types required for each application.  Where more than single type is specified for an application, selection is Installer’s option, but provide a unified manufacturer selection for each application.

B.		Color-Coded Plastic Tape:

1.	Provide manufacturer’s standard self-adhesive vinyl tape not less than 3 mils thick by 1-1/2” wide.  Provide color as required to identify conductor phase.

C.		Cable/Conductor Identification Bands:

1.	Wire Markers: For control circuits, provide computer-generated vinyl or plastic sleeve, slipover type, white background with black imprinting as required for specific application.

2.	Color-Coded Plastic Tape: For power circuits, provide manufacturer’s standard self-adhesive vinyl tape.  Unless otherwise indicated, provide colors according to applicable codes or standards.

D.		Operational Instructions and Warnings:

1.	Provide manufacturer’s standard pre-printed, accident-prevention and operational tags, of plasticize card stock with matte finish suitable for writing, approximately 3-1/4” x 5-5/8”, with brass grommets and wire fasteners, and with appropriate pre-printed wording including large-size primary wording (as examples:  “DANGER”, CAUTION, DO NOT OPERATE”).

2.	Provide manufacturer’s standard, self-adhesive or pressure-sensitive, pre-printed, flexible vinyl signs for operational instructions or warnings, of sizes suitable for application areas and adequate for visibility, with proper wording for each application (as examples:  “208V”, EXHAUST FAN”, “RECTIFIER”).  Unless otherwise indicated or required by governing regulations, provide orange signs with black lettering.

3.	Provide arc-flash hazard warning labels on all electrical distribution equipment in accordance with NFPA 70E and NFPA 70 (National Electrical Code) requirements.

E.		Danger and Caution Signs:

1.	Provide manufacturer’s standard “DANGER” signs of baked enamel finish on 20-gage steel, of standard red, black and white graphics, 14” x 10” size except where 10” x 7” is the largest size which can be applied where needed and except where larger size is needed for adequate vision, and with/wording: “DANGER HIGH VOLTAGE UNAUTHORIZED PERSONNEL KEEP OUT.”

2.	Provide manufacturer’s standard “CAUTION” signs of pressure sensitive polyester, with adhesive back coating, 2-1/4” x 9”.

F.		Equipment/System Identification Signs:

1.	Provide engraved stock melamine plastic-laminate, complying with FS L-P-387, in sizes and thicknesses indicated, engraved with engraver’s standard letter style of sizes and wording indicated black and white core (letter color) except as otherwise indicated, punched for mechanical fastening except where adhesive mounting is necessary because of substrate.

All panels, disconnect switches, contactors, starters, timers, control panels, and each individual load in motor control centers and switchboards, shall be identified with engraved, plastic laminate labels.  Embossed tape labels are not acceptable.  All labels shall be sized to accommodate the lettering.  Labels shall have white lettering on a black field, unless shown otherwise.

EXAMPLE:  	PANEL “A”

120/240 VOLTS, 1, 3W

100 AMPS - M.L.O.

FED FROM “MFDS”

INSTALLED 3/2005

The labels shall be secured to the front cover of the device using poprivets, smooth side outside the enclosure cover, or “RTV” type clear silicone sealant, completely covering the rear of the label.  Glue or double-sided tape is not acceptable.

The Contractor shall submit to the Architect/Engineer a schedule of proposed equipment labels for review, amending and approval, before making the labels.

2.	Thickness:  1/16”, for units up to 20 sq. in. or 8” length, 1/8” for larger units.

G.		Fasteners:  Self-tapping stainless steel screws, except contact-type permanent adhesive where screws cannot or should not penetrate substrate.

2.02	LETTERING AND GRAPHICS

A.		Coordinate names, abbreviations and other designations used in electrical identification work, with corresponding designations shown, specified or scheduled.  Provide numbers, lettering and wording as indicated or, if not otherwise indicated, as recommended by manufacturers or as required for proper identification and operation/maintenance of electrical systems and equipment.

PART 3 - EXECUTION

3.01	APPLICATION AND INSTALLATION:

A.		General Installation Requirements:

1.	Coordination:  Where identification is to be applied to surfaces, which require finish, install identification after completion of painting.

2.	Regulations:  Comply with governing regulations and requests of governing authorities for identification of electrical work.

B.		Cable/Conductor Identification:

1.	Apply cable/conductor identification on each cable and conductor (line and load) in each box/enclosure/cabinet where wires are present, except where another form of identification (such as color-coded conductors) is provided.  Match identification with marking system used in panelboards, shop drawings, contract documents, and similar previously established identification for project electrical work.

2.	Conductors shall be clearly and permanently identified.

3.	All control circuit and instrument circuit terminations shall be identified on both ends of each conductor according to control drawing.

4.	For conductors #6 and smaller, conductor color-coding shall be color insulation.  For conductor color-coding of wire larger than #6, use self-adhesive wraparound tape markers.  Use markers at all panelboards, transformers, boxes, outlets, switches, circuit breakers and control centers.

5.	All grounding conductors and these only: Green.

C.		Equipment/System Identification Signs:

1.	Provide engraved plastic-laminate, in sizes and thicknesses indicated, engraved with engraver’s standard letter style of sizes and wording indicated black and white core (letter color; except as otherwise indicated, punched for mechanical fastening except where adhesive mounting is necessary because of substrate.

2.	Thickness:  1/16” for units up to 20 sq. in. or 8” in length, 1/8” for larger units.

D.		Fasteners:  Self-tapping stainless steel screws, except use contact-type permanent adhesive where screws cannot or should not penetrate substrate.

3.02	LETTERING AND GRAPHICS:

A.		Coordinate names, abbreviation and other designations used in electrical identification work, with corresponding designations shown, specified or scheduled.  Provide numbers, lettering and wording as indicated or, if not otherwise indicated, as recommended by manufacturers or as required for proper identification and operation/maintenance of electrical systems and equipment.

B.		Junction Box Identification:

1.		Apply panel and circuit identification numbers on the cover of all boxes.  Utilize black lettering for normal power circuits and red lettering for emergency power circuits (use indelible ink marker pens).

C.		Equipment/System Identification: Install engraved plastic-laminate sign on each major unit of electrical equipment in building unless unit is specified with its own self-explanatory identification.  Except as otherwise indicated, provide single line of text, ½” high lettering on 1-1/2” high sign (2” high where 2 lines are required), white lettering in black field or white letters in red field for emergency circuits.  Provide text matching terminology and numbering of the contract documents and shop drawings.  Provide signs for the following pieces of electrical equipment:

- Panelboards, electrical cabinets and enclosures.

- Disconnect switches.

- Starters and associated motors.

- Large junction boxes.

e.	Special application control switches.

D.		Install signs at locations indicated, or, where not otherwise indicated, at location for best convenience of viewing without interference with operation and maintenance of equipment.  Secure to substrate with fasteners, except use adhesive where fasteners should not or cannot penetrate the substrate.

## END SECTION -