SECTION 03200

CONCRETE REINFORCEMENT

PART 1	GENERAL

1.01	SCOPE OF WORK

A.	Furnish all labor, materials, equipment and incidentals required and install all concrete reinforcement complete as shown on the Drawings and as specified herein.

B.	Furnish only all deformed steel reinforcement required to be entirely built into concrete masonry unit construction.

1.02	RELATED WORK

A.	Concrete Formwork is included in Section 03100.

B.	Concrete Joints and Joint Accessories are included in Section 03250.

C.	Cast-in-place Concrete is included in Section 03300.

D.	Grout is included in Section 03600.

1.03	SUBMITTALS

A.	Submit to the Engineer, in accordance with Section 01300, shop drawings and product data showing materials of construction and details of installation, including the following:

1.	Reinforcing steel placing drawings. Placing drawings shall conform to the recommendations of ACI 315. Clearly identify the portion of the Work covered by each placing drawing. All bar splice locations and lap lengths shall be clearly shown. Clearly show the placement of all required additional reinforcement (around openings, at corners, etc.) as shown on the Drawings.

2. 	Bill of materials (bar list). Clearly show the placement of each bar listed in the bill of materials on the placing drawings.

3. 	Bar bending details. The bars shall be referenced to the same identification marks shown on the placing drawings. Include standard bending diagrams in the submittal, as applicable.

4. 	Identify the grade of reinforcing steel in the submittal. Clearly identify any bars that are of a different grade or that have special coatings.

B.	Submit Test Reports, in accordance with Section 01300, of each of the following items:

1.	Certified copy of mill test on each steel proposed for use showing the physical properties of the steel and the chemical analysis.

2.	Welder's certification.  The certification shall be in accordance with AWS D1.4 when welding of reinforcement required.

1.04	REFERENCE STANDARDS

A.	American Society for Testing and Materials (ASTM)

1.	ASTM A82 - Standard Specification for Steel Wire, Plain, for Concrete Reinforcement.

2.	ASTM A184 - Standard Specification for Fabricated Deformed Steel Bar Mats for Concrete Reinforcement.

3.	ASTM A185 - Standard Specification for Steel Welded Wire Fabric, Plain, for Concrete Reinforcement

4.	ASTM A496 - Standard Specification for Steel Wire, Deformed, for Concrete Reinforcement

5.	ASTM A497 - Standard Specification for Steel Welded Wire Fabric, Deformed, for Concrete Reinforcement

6.	ASTM A615 - Standard Specification for Deformed and Plain Billet-Steel Bars for Concrete Reinforcement

7.	ASTM A706 - Standard Specification for Low-Alloy Steel Deformed and Plain Bars for Concrete Reinforcement.

B.	American Concrete Institute (ACI)

1.	ACI 301 - Standard Specification for Structural Concrete

2.	ACI 315 - Details and Detailing of Concrete Reinforcement.

3.	ACI 350 - Building Code Requirements for Environmental Concrete Structure

4.	ACI SP-66 - ACI Detailing Manual

C.	Concrete Reinforcing Steel Institute (CRSI)

- Manual of Standard Practice

D.	American Welding Society (AWS)

1.	AWS D1.4 - Structural Welding Code - Reinforcing Steel

E.	Where reference is made to one of the above standards, the revision in effect at the time of bid opening shall apply.

1.05	DELIVERY, HANDLING AND STORAGE

A.	Reinforcing steel shall be substantially free from mill scale, rust, dirt, grease, or other foreign matter.

B.	Reinforcing steel shall be shipped and stored with bars of the same size and shape fastened in bundles with durable tags, marked in a legible manner with waterproof markings showing the same "mark" designations as those shown on the submitted Placing Drawings.

C.	Reinforcing steel shall be stored off the ground, protected from moisture and kept free from dirt, oil, or other injurious contaminants.

PART 2	PRODUCTS

2.01	MATERIALS

A.	Materials shall be new, of domestic manufacture and shall comply with the following material specifications.

B.	Deformed Concrete Reinforcing Bars:  ASTM A615, Grade 60 deformed bars.

C.	Concrete Reinforcing Bars required on the Drawings to be Welded:  ASTM A706.

D.	Spiral Reinforcement

1.	ASTM A615, Grade 60 for hot-rolled plain or deformed bars.

2.	ASTM A82 for cold-drawn wire.

- Welded Steel Wire Fabric:  ASTM A185. Provide in flat sheets.

F.	Welded Deformed Steel Wire Fabric:  ASTM A497.

G.	Welded Plain Bar Mats:  ASTM A704 and ASTM A615 Grade 60 plain bars.

H.	Fabricated Deformed Steel Bar Mats:  ASTM A184 and ASTM A615 Grade 60 deformed bars.

I.	The following alternate materials are allowed:

1.	ASTM A615 Grade 60 may be used for ASTM A706 provided the following requirements are satisfied:

a.	The actual yield strength of the reinforcing steel based on mill tests shall not exceed the specified yield strength by more than 18,000 psi.  Retests shall not exceed this value by more than an additional 3000 psi.

b.	The ratio of the actual ultimate tensile strength to the actual tensile yield strength of the reinforcement shall not be less than 1.25.

c.	The carbon equivalency (CE) of bars shall be 0.55 or less.

J.	Reinforcing Steel Accessories

1.	Plastic Protected Bar Supports:  CRSI Bar Support Specifications, Class 1 - Maximum Protection.

2.	Stainless Steel Protected Bar Supports:  CRSI Bar Support Specifications, Class 2 - Moderate Protection.

3.	Precast Concrete Block Bar Supports:  CRSI Bar Support Specifications, Precast Blocks.  Blocks shall have equal or greater strength than the surrounding concrete.

K.	Tie Wire

1.	Tie Wires for Reinforcement shall be 16-gauge or heavier, black annealed wire.

L.	Fiber Reinforcement

1.	Synthetic reinforcing fiber for concrete shall be 100 percent polypropylene collated, fibrillated fibers as manufactured by Fibermesh Company of Synthetic Industries Inc., Chattanooga, TN – Fibermesh or equal.  Fiber length and quantity for the concrete mix shall be in strict compliance with the manufacturer’s recommendations as approved by the Engineer.  Synthetic fibers shall conform to ASTM C 1116 / C 1116M, Type III, Synthetic Fiber, and as follows.  Fibers shall be 100 percent virgin polypropylene fibrillated fibers containing no reprocessed olefin materials.  Fibers shall have a specific gravity of 0.9, a minimum tensile strength of 70 ksi graded per manufacturer, and specifically manufactured to an optimum gradation for use as concrete secondary reinforcement

2.02	FABRICATION

A.	Fabrication of reinforcement shall be in compliance with the CRSI Manual of Standard Practice and ACI 315.

B.	Bars shall be cold bent.  Bars shall not be straightened or rebent.

C.	Bars shall be bent around a revolving collar having a diameter of not less than that recommended by the ACI 318.

D.	Bar ends that are to be butt spliced, placed through limited diameter holes in metal, or threaded, shall have the applicable end(s) saw-cut.  Such ends shall terminate in flat surfaces within 1-1/2 degrees of a right angle to the axis of the bar.

E.	Spirals

1.	Provide a minimum of 1-1/2 finishing turns at the top and bottom.

2.	Splices shall be tension lap splices at least 48 bar diameters, but not less than 12-in in length.  Welded splices shall only be used where specifically approved by the Engineer.

3.	Provide spacers as recommended by the CRSI.

PART 3	EXECUTION

3.01	INSTALLATION

A.	Surface condition, bending, spacing and tolerances of placement of reinforcement shall comply with the CRSI Manual of Standard Practice and ACI 301.  The Contractor shall be solely responsible for providing an adequate number of bars and maintaining the spacing and clearances shown on the Drawings.

B.	Except as otherwise indicated on the Drawings, the minimum concrete cover of reinforcement shall be as follows:

1.	Concrete cast against and permanently exposed to earth:  3-in

2.	Concrete exposed to soil, water, sewage, sludge and/or weather:  2-in

(including bottom cover of slabs over water or sewage)

3.	Concrete not exposed to soil, water, sewage, sludge and/or weather:

a.	Slabs (top and bottom cover), walls, joists, shells and folded plate members - 1-in

b.	Beams and columns (principal reinforcement, ties, spirals and stirrups) - 1-1/2-in

C.	Reinforcement which will be exposed for a considerable length of time after being placed shall be coated with a heavy coat of neat cement slurry.

D.	No reinforcing steel bars shall be welded either during fabrication or erection unless specifically shown on the Drawings or specified herein, or unless prior written approval has been obtained from the Engineer.  All bars that have been welded, including tack welds, without such approval shall be immediately removed from the work.  When welding of reinforcement is approved or called for, it shall comply with AWS D1.4.

E.	Reinforcing steel interfering with the location of other reinforcing steel, conduits or embedded items may be moved within the specified tolerances or one bar diameter, whichever is greater.  Greater displacement of bars to avoid interference shall only be made with the approval of the Engineer.  Do not cut reinforcement to install inserts, conduits, mechanical openings or other items without the prior approval of the Engineer.

F.	Securely support and tie reinforcing steel to prevent movement during concrete placement. Secure dowels in place before placing concrete.

G.	Reinforcing steel bars shall not be field bent except where shown on the Drawings or specifically authorized in writing by the Engineer.  If authorized, bars shall be cold-bent around the standard diameter spool specified in the CRSI.  Do not heat bars.  Closely inspect the reinforcing steel for breaks.  If the reinforcing steel is damaged, replace, Cadweld or otherwise repair as directed by the Engineer.  Do not bend reinforcement after it is embedded in concrete.

3.02	REINFORCEMENT AROUND OPENINGS

A.	Unless specific additional reinforcement around openings is shown on the Drawings, provide additional reinforcing steel on each side of the opening equivalent to one half of the cross-sectional area of the reinforcing steel interrupted by an opening.  The bars shall have sufficient length to develop bond at each end beyond the opening or penetration.

3.03	SPLICING OF REINFORCEMENT

- Lap splices shall be provided as shown on the Drawings.  For lap splices not shown, request clarification from the Engineer.  (In general, lap splices will be required to be Class B tension lap splices in accordance with ACI 350.

B.	Install wire fabric in as long lengths as practicable.  Splices in welded wire fabric shall be lapped in accordance with the requirements of ACI 350 but not less than 12-in.  The spliced fabrics shall be tied together with wire ties spaced not more than 24-in on center and laced with wire of the same diameter as the welded wire fabric.  Do not position laps midway between supporting beams, or directly over beams of continuous structures.  Offset splices in adjacent widths to prevent continuous splices.

3.04	ACCESSORIES

A.	Determine, provide and install accessories such as chairs, chair bars and the like in sufficient quantities and strength to adequately support the reinforcement and prevent its displacement during the erection of the reinforcement and the placement of concrete.

B.	Use precast concrete blocks where the reinforcing steel is to be supported over soil.

C.	Stainless steel bar supports or steel chairs with stainless steel tips shall be used where the chairs are set on forms for a concrete surface that will be exposed to weather, high humidity, or liquid (including bottom of slabs over liquid containing areas).  Use of galvanized or plastic tipped metal chairs is permissible in all other locations unless otherwise noted on the Drawings or specified herein.

D.	Alternate methods of supporting top steel in slabs, such as steel channels supported on the bottom steel or vertical reinforcing steel fastened to the bottom and top mats, may be used if approved by the Engineer.

3.05	INSPECTION

A.	In no case shall any reinforcing steel be covered with concrete until the installation of the reinforcement, including the size, spacing and position of the reinforcement has been observed by the Engineer and the Engineer's release to proceed with the concreting has been obtained.  The Engineer shall be given ample prior notice of the readiness of placed reinforcement for observation.  The forms shall be kept open until the Engineer has finished his/her observations of the reinforcing steel.

END OF SECTION