SECTION 05100

STRUCTURAL STEEL

PART 1 - GENERAL

1-01	SCOPE:

A.	The Work of this Section shall consist of furnishing all the labor, materials, and equipment necessary for installation of structural steel as shown on the Drawings and as specified herein.

1-02	CONDITIONS OF THE CONTRACT APPLY:

1-03	SHOP DRAWINGS AND ERECTION PROCEDURES:

A. 	Prepare and submit shop and erection plans covering all structural steel and related items.  All dimensions for checking of structural steel details shall be shown on the drawings. Plans identify the OWNER furnish Catwalk assemblies that shall be erected by Contractor as shown on the Drawings. OWNER will furnish shop drawings; but Contractor shall submit his erection plans on installing the OWNER furnished Catwalks assemblies.

B. 	The Contractor shall be responsible for the conformation of all steel details to the typical and special details shown on the drawings.  All details, notes and schedules appearing on the drawings, and giving information for the fabrication and erection of the structural steel and related items shall be shown also on the erection or shop drawings.  Drawing shall include all shop and erection details, including cuts, copes, connections, holes, bolts and welds.  For bolted connections, the type, size and length of bolts including washers shall be shown.  All welds, both shop and field, shall be indicated by standard welding symbols as noted by AWS A2.0.  Drawings shall show the size, length and type of each weld.

C. 	Prepare and submit, for information, two copies of a detailed erection procedure with the shop and erection drawings.  The procedure shall include the sequence of erection with temporary staying and bracing.  No copies of such procedures will be returned.

D.	Prepare and submit for approval, two copies of the detailed erecting and installation sequence of the back flow slide and flap gates, and engine exhausts for engines 1 thru 5.

1-04	APPLICABLE SPECIFICATIONS AND CODES:

A.	The following specifications and codes form a part of this section of these specifications:

1.	American Institute of Steel Construction Publications, Latest Edition, with Commentary.

a.	Code of Standard Practice for Steel Buildings and Bridges.

b.	Specification for the Design, Fabrication and Erection of Structural Steel for Buildings, with Commentary.

c.	Manual of Steel Construction.

2.	American Society for Testing and Materials:

a.	A992 - Specifications for Structural Steel Wide Flange (W) Shape only and A36 – Fy=50 ksi for all Other Shapes and Steel Plate except (HP).

b.	A307 - Specification for Low-Carbon Steel Externally Threaded Standard Fasteners for Fit-up only and Cast-in-Place Anchor Bolts.

c.	A500 Gr. B - Specification for Hot-Formed Welded and Seamless Carbon Steel Structural Tubing.

d.	A325 - Specification for High-Strength Steel Bolts for Structural Steel, Joints, Including Suitable Nuts and Plain Hardened Washers.

e.	E329 - Recommended Practice for Inspection and Testing Agencies for Concrete, Steel and Bituminous Materials as Used in Construction.

3.	American Welding Society:

a.	D1.1 - Code for Welding in Building Construction.

4.	Specifications for Structural Joints Using ASTM A325 of A490 bolts, approved April 1978, by the Research Council on Riveted and Bolted Structural Joints of the Engineering Foundation.

5.	Unless otherwise indicated on the drawings, the Specification for the Design, Fabrication, and Erection of Structural Steel for Buildings of the American Institute of Steel Construction, hereafter designated AISC, shall govern structural steel work.  Welding shall be in accordance with American Welding Society Standard Code D1.1.

1-05	SUBSTITUTIONS OF SECTIONS:

- Substitutions of sections or modifications of details, or both, and the reasons therefore, shall be submitted with the shop drawings for approval.  Approved substitutions, modifications, and changes in related portions of the work shall be coordinated by the Contractor and shall be accomplished at no additional cost to the Owner.

1-06	RESPONSIBILITY FOR ERRORS:

A.	The Contractor shall be responsible for all errors of detailing, fabrication, and for correct fitting measurements in the field to verify or supplement dimensions shown on the drawings and shall assume responsibility for fitting new work to existing work.

1-07	TEMPLATES:

A.	Templates shall be furnished by the Fabricator to the job, together with instructions for the setting of anchors, anchor bolts and bearing plates.  The Contractor shall ascertain that the items are set during the progress of the work.

1-08	QUALIFICATION:

A.	Fabrication Shop and Erection personnel shall have fabricated and erected projects of similar size and complexity for at least five years.

B.	Welders and Welding Operators, shop and field, shall be qualified by an independent laboratory using test procedures covered by an independent laboratory using test procedures covered in AWS D1.1, and shall have been employed as a welder using the positions for which he is qualified during the previous 90 days.  The Contractor shall provide the Engineer and the laboratory inspector with the names of welders to be employed in the shop and field on the work, certification of the position, date of the last qualification test and the name of the qualifying laboratory.

1. 	All welders employed in the shop on the fabrication of the steel work shall be qualified for the most difficult welding position during shop fabrication.

2. 	All welders employed in the field on the erection of the steel work shall be qualified for the most difficult welding position during field erection.

3. 	The Contractor shall require any welder to retake the test, when, in the opinion of the Engineer, the work of the welder creates a reasonable doubt as to the proficiency of the welder.  Recertification of the welder shall be made to the Engineer only after the welder has taken and passed the specified test.  The Engineer may require radiographic or ultrasonic testing or may require coupons to be cut from any location in any joint for testing.

4. 	Should any two radiographic or ultrasonic tests or coupons cut from the work of any welder show strengths, under tests, less than that of the base metal, it will be considered evidence of negligence or incompetence and such welder shall be removed from the work.

5. 	When coupons are removed from any part of a structure, the members cut shall be repaired, at no additional cost to the Owner, in a neat and workmanlike manner with joints of type to develop the full strength of the members and joints cut, with peening to relieve residual stress.  All sections of welds found defective shall be chipped or cut out to base metal and rewelded before proceeding with the work.

6. 	Costs of all qualifications, tests and retests shall be borne by the Contractor.

C.	Joint Qualification:  All joints shall comply with AWS D1.1.

1-09	INSPECTION AND TESTING:

A.	Inspections and tests shall be performed by an independent laboratory complying with ASTM E329, selected, directed by the Engineer, and paid by the Owner.  All material to be furnished shall be subject to inspections and tests in the shop and field.

B.	Shop inspections and tests shall include fit-up, preparation of surfaces and welding.

C.	Field inspections and tests shall include fit-up, preparation of surface, welding and bolting.

D.	Reports of shop and field inspections and testing shall be made by the laboratory on a weekly basis and submitted directly as follows:  One copy each to the Structural Engineer, Resident Engineer Inspector, Contractor, Fabricator and Erector.

PART 2 - PRODUCTS

2-01	GENERAL:

A.	Materials shall be of domestic manufacture, within trade tolerances, new, undamaged and without splices.  Structural material, plain or fabricated, shall be stored above the ground upon platforms, skids or supports.  Material shall be kept free of dirt, grease and foreign matter and shall be protected from corrosion.

2-02	STRUCTURAL STEEL:

A. 	Structural steel shall comply with ASTM A709 GR50W, Fy+50kx, Except gusset plates, stiffeners, bracing, and other secondary members shall be ASTM A709 GR 36 steel, ASTM A36, and ASTM A500.

B. 	The Contractor shall furnish two copies of all mill reports covering the chemical and physical properties of the steel used.

2-03	BOLTS, NUTS AND WASHERS:

A.	All bolts, nuts and washers shall comply with ASTM A307 and A325.

B.	ASTM F593 threaded fasteners shall be used for all anchor bolts set in concrete.

C. 	ASTM A307 and A325 bolts shall be used for connections as indicated on the drawings.

2-04	WELDING EQUIPMENT:

A.	Welding equipment shall be capable of providing the welding required by the drawings or specifications herein in accordance with the requirements of joint qualifications in AWS D1.1.

2-05	WELDING ELECTRODES:

A.	Electrodes and flux used for submerged arc welding shall be of the same manufacture.  The flux shall be free of contamination from dirt, mill scale and foreign material.  Fused flux used in welding shall not be reused.  Bare electrodes and flux used in combination shall conform to the requirements of AWS D1.1.

B.	Electrodes for manual shielded metal-arc welding shall conform to AWS D1.1.

2-06	COATING:

### 2-07	GROUTS:

A.	Non-shrink grout Vendors beneath base and bearing plates shall be either Five Star Grout by U.S. Grout Corp; Sonogrout by L. Sonneborn Inc., Horn Non-Metallic Grout by A.C. Horn Inc., or Non-Ferrous Non-Shrink Grout by the Burke Co. or approved equal.  Follow requirements of Section 03600.  Contractor shall submit Vendor for approval by Engineer prior to use.

2-08	FABRICATION:

A.	Structural material shall be fabricated and assembled in the shop.  Assembled pieces shall be taken apart for the removal of burrs and shavings produced by the reaming operation.  Parts not connected in the shop shall be secured by bolts to prevent damage in shipment and handling.

B.	Connections shall be as shown on the drawings.  Connections not indicated shall be made to conform to the AISC Specifications.  One-sided or other types of eccentric connections will not be permitted except where shown on the plans.  Surfaces of joints for welded and bolted connections shall be clean, bright metal.  Fit-up of the parts shall be inspected and approved by the laboratory inspector prior to making final connection.

1. 	Holes shall be cut, drilled or punched at right angles to the surface of the metal and shall not be made or enlarged by burning.  Holes in base or bearing plates shall be drilled.  Holes shall be clean-cut without torn or ragged edges.  Outside burrs resulting from drilling or reaming operation shall be removed.  Holes for bolts shall be 1/16 inch larger than the diameter of the bolt.

2. 	ASTM 307 bolts transmitting shear shall be threaded to such a length that no more than one thread will be within the grip of the metal.  The bolts shall be of the length that will extend through, but no more than 1/4 inch beyond the nut.  Nuts shall be tightened while bolt heads are tapped with a hammer.  Tightening shall progress outward from the center of the joint.  Nuts shall be locked after final tightening.

3. 	Welded connections will be permitted only where indicated on the drawings.  Welded construction shall conform to the AISC and AWS Specifications.

4.      Bolted connections using ASTM A325 bolts shall conform to the Specifications for Structural Joints using ASTM A325 or A490 bolts.  Bolt threads shall be excluded from the shear planes of the contact surfaces between the connected parts and the bolts shall be tightened by the "Turn-of-Nut" method.

C.	Milled surfaces shall comply with the AISC Specification and the drawings.

D. 	Allowance shall be made for draw in all tension bracing.

PART 3 - EXECUTION

3-01	STRUCTURAL STEEL:

A. 	Splices and field connections shall be made as shown or noted on the drawings.  Errors in shop fabrication of deformation resulting from handling and transportation that prevent the assembly and fitting of parts shall be reported immediately to the Engineer for directions as to method of correction.  Corrections shall be made at no additional cost to the Owner.

B. 	Leveling plates shall not be used under base plates.

C. 	Anchor bolts and anchors shall be located and built into connecting work.  Bolts and anchors shall be preset by the use of templates to locate the anchors and anchor bolts.

D. 	Column bases and bearing plates shall be attached as shown on the drawings.  Plates shall be supported and aligned on steel wedges or shims.  After the supported members have been plumbed and positioned and the anchor nuts tightened, the entire bearing area under the plate shall be dry-packed solidly with non-shrink grout.  Wedges and shims shall be cut off flush with edge of column base and bearing plates, and shall be left in place.

E. 	After assembly, the various members forming parts of a completed frame or structure shall be aligned and adjusted before being fastened.  Tolerance shall conform to AISC.  Fastening of splices of compression members shall be done after the abutting surfaces have been brought completely into contact.  Bearing surfaces and surfaces that will be in permanent contact shall be cleaned before the members are assembled.  As erection progresses, the work shall be fastened to take care of all dead load, wind and erection stresses.  Splices will be permitted only where indicated on the drawings.  Erection bolts used in welded construction shall be tightened and left in place.  Welding for redrilling will not be permitted.

F. 	Driftpins may be used only to bring together the several parts, and shall not be used in such manner as to distort or damage the metal.

G. 	The use of a gas-cutting torch in the field for correcting fabrication errors is prohibited unless the Engineer has specifically approved such procedures for each case individually in writing.

3-02	PAINTING:

A.	All steel work shall be cleaned of loose mill scale, loose rust, accessible weld slag or flux deposit, dirt, and foreign matter.  Solvent shall remove oil and grease deposits.  No paint shall be applied when steel temperature is below the dew point of the atmosphere.  Paint shall be mixed and no pigment shall remain on bottom of can.

B.	After cleaning and connections are approved by the inspector, all steel work except that to be encased in concrete, surfaces to be fireproofed, or surfaces to be welded or bolted shall be given a shop coat of primer.  The primer shall be applied at a rate to provide a minimum dry film of two (2.0) mils.  The primer shall be applied without holidays or paint runs.

C.	After erection, all field connections shall be cleaned.  All connections, including welds and bolts, and all abraded surfaces on the shop primer shall be painted to give one complete coat primer. Paint for field touch-up shall be the same paint used for the shop coat.

PART 4 - MEASUREMENT AND PAYMENT

4-01	The measurement for payment for steel tie-in assemblies fabricated, erected and placed will be based upon EACH complete installed or erected assembly properly installed. Price and payment shall constitute full compensation for furnishing all plant, labor, materials, including fasteners, anchor bolts and welding, fabricating, coating, consumables and equipment for performing satisfactory placement of each Assembly. Payment for each Assembly shall be made under the cost of each Assembly Bid Item.

***END OF SECTION***